## Calculator
[10 empty] | MTBF | [9 empty] | Average Main supply outage (per year) | 8
|  |  |  | 8.393% |  |  |  | UPS | 100000 | [10 empty] | Main supply outage average duration (in hours) | 1
|  |  |  | 2.168% |  |  |  | UPS Bypass | 400000 | [10 empty] | Cost loss of Production (in $ per hour) | 10000
|  |  |  | 19.68% |  |  |  | Generator | 40000 | [10 empty] | Average duration to recover a full system failure (in hours) | 4
|  | 25.34% | [5 empty] | Main/Generator change-over | 30000 | [10 empty] | Average cost to recover a full system failure (in $ per recovery) | 5000
|  |  |  | 1.09% |  |  |  | STS | 800000 | [10 empty] | Number of critical loads | 4
1st year | Per year
Risk Load | Risk Fin.
10.38% | 45650.1048 |  | MAIN | [5 empty] | LOAD 1
Risk System | [8 empty] | 10.38%
10.38% |  |  |  |  | By Pass
2.168%
[5 empty] | UPS |  |  |  | LOAD n
[5 empty] | 8.393% |  |  |  | 10.38%
Risk Load | Risk Fin.
5.455% | 23992.1074 |  | MAIN
System
5.455% |  |  |  |  | Change Over |  | 40.03% | [6 empty] | LOAD 1
[5 empty] | 25.34% | [8 empty] | 5.455%
|  |  | GENERATOR | [5 empty] | By Pass
|  |  | 19.68% | [5 empty] | 2.168%
[9 empty] | UPS |  |  |  |  | LOAD n
[9 empty] | 8.393% |  |  |  |  | 5.455%
Risk Load | Risk Fin.
3.855% | 16958.1352 |  | MAIN
Risk System
3.855% |  |  |  |  | STS |  | 20.56% | [6 empty] | LOAD 1
[5 empty] | 1.09% | [8 empty] | 3.855%
|  |  | GENERATOR | [5 empty] | By Pass
|  |  | 19.68% | [5 empty] | 2.168%
[9 empty] | UPS |  |  |  |  | LOAD n
[9 empty] | 8.393% |  |  |  |  | 3.855%
Risk Load | Risk Fin.
2.796% | 12298.7905 |  | MAIN
Risk System
2.796% |  |  |  |  | STS |  | 20.56% | [9 empty] | LOAD 1
[5 empty] | 1.09% | [11 empty] | 2.796%
|  |  | GENERATOR | [9 empty] | STS
|  |  | 19.68% | [9 empty] | 1.09%
[9 empty] | UPS | [7 empty] | LOAD n
[9 empty] | 8.393% | [7 empty] | 2.796%
Risk Load | Risk Fin.
2.155% | 9479.5406 |  |  |  |  | By Pass |  | 10.38%
Risk System | [5 empty] | 2.168% | [7 empty] | LOAD 1
2.155% |  |  | MAIN |  |  | UPS | [7 empty] | 2.155%
[6 empty] | 8.393% |  |  | STS
1.09%
LOAD n
[6 empty] | By Pass |  | 10.38% | [5 empty] | 2.155%
2.168%
UPS
8.393%
Risk Load | Risk Fin.
2.796% | 7588.1165 |  | MAIN
Risk System
1.725% |  |  |  |  | STS |  | 20.56%
1.09%
|  |  | GENERATOR | [9 empty] | STS |  |  | LOAD 1 |  |  | STS | LOAD n
|  |  | 19.68% | [9 empty] | 1.09% |  |  | 2.796% |  |  | 1.09% | 2.796%
UPS
8.393%
Risk Load | Risk Fin.
1.786% | 3098.3035 |  | MAIN
Risk System
0.7044% |  |  |  |  | UPS
8.393%
[8 empty] | STS |  |  |  | LOAD 1 |  |  | STS |  |  | LOAD n
[8 empty] | 1.09% |  |  |  | 1.786% |  |  | 1.09% |  |  | 1.786%
UPS
8.393%
Risk Load | Risk Fin.
1.343% | 1124.9809 |  | MAIN
Risk System
0.2558% | [7 empty] | STS |  |  | 9.391%
1.09%
|  |  | Change Over |  | UPS | [7 empty] | STS |  |  | LOAD 1 |  |  | STS | LOAD n
[5 empty] | 8.393% | [7 empty] | 1.09% |  |  | 1.343% |  |  | 1.09% | 1.343%
[8 empty] | STS |  |  | 2.723%
1.09%
GENERATOR
19.68%
Risk Load | Risk Fin.
1.256% | 737.9447 |  | MAIN
Risk System
0.1678% | [7 empty] | STS |  |  | 9.391%
1.09%
[5 empty] | UPS | [7 empty] | STS |  |  | LOAD 1 |  |  | STS | LOAD n
[5 empty] | 8.393% | [7 empty] | 1.09% |  |  | 1.256% |  |  | 1.09% | 1.256%
[8 empty] | STS |  |  | 1.786%
1.09%
UPS
8.393%

## Sheet3 (hidden)
UPS MTBF
120000
100000
80000
60000
40000
GENERATOR MTBF
60000
50000
40000
30000
20000
Change-Over
50000
40000
30000
20000
10000
iSTS
800000
600000
400000
200000
100000